## Table_1
No | Scenario name | Collection type | WWTP con fi guration | Urine post-treatment
1 | REF | Conventional sewer | Conventional (AS + AD) | e
2 | EPC | Conventional sewer | Enhanced primary clarification | e
3 | USS | Urine separated | Conventional (AS + AD) | Struvite precipitation þ reinjection
4 | USS þ EPC | Urine separated | Enhanced primary clarification | Struvite precipitation þ reinjection
5 | USS þ EPC þ AGRI | Urine separated | Enhanced primary clarification | Struvite precipitation þ agricultural application
6 | USS þ EPC þ ANA | Urine separated | Enhanced primary clarification | Struvite precipitation þ nitritation/deammonification

## Table_2
Parameter | Unit | Ecoinvent 2.2 a | Tchobanoglous et al. (2003) ,b | Corominas et al. (2013b) ,b | This study (dynamic REF)
Electricity consumed by the WWTP | kWh m^-3 sewage | 0.28 | 0.39 | 0.18 x 10^0 | 0.31
Biogas produced | Nm^3 m^-3 sewage | 0.068 | 0.053 | 0.069 x 10^0 | 0.058

## Table_3
Scenarios.Scenarios | Ef fl uent total N (gNm  3 ).364 d-Average | Ef fl uent total N (gNm  3 ).Maximum daily average | Ef fl uent total N (gNm  3 ).Violations (days) | Ef fl uent total P (gP m  3 ).364 d-Average | Ef fl uent total P (gP m  3 ).Maximum daily average | Ef fl uent total P (gP m  3 ).Violations (days) | Ef fl uent total COD (gCODm  3 ).364 d-Average | Ef fl uent total COD (gCODm  3 ).Maximum daily average
Steady state REF | 6.31 | 6.31 | 6.31 | 0.56 | 0.56 | 0.56 | 39.1 | 39.1
REF | 8.13 | 14.64 | 30 | 0.64 | 1.62 | 15 | 40.8 | 68.7
EPC | 6.39 | 13.10 | 5 | 0.41 | 1.14 | 2 | 44.1 | 71.1
USS | 6.93 | 11.82 | 9 | 0.55 | 1.36 | 7 | 41.5 | 67.1
USS þ EPC | 6.51 | 11.96 | 5 | 0.35 | 0.99 | 0 | 43.5 | 70.6
USS þ EPC þ AGRI | 6.59 | 10.38 | 2 | 0.36 | 1.003 | 1 | 37.7 | 64.5
USS þ EPC þ ANA | 7.23 | 10.32 | 2 | 0.47 | 1.18 | 6 | 40.4 | 66.2
Scenarios | fl uent total NH 4 (gNm  3 ) | fl uent total NH 4 (gNm  3 ) | fl uent total NH 4 (gNm  3 ) | fl uent total suspended solids (gTSS m  3 ) | fl uent total suspended solids (gTSS m  3 ) | fl uent total suspended solids (gTSS m  3 ) | Methanol dosage 3 1 FeCl 3 dosage 3  1 | Methanol dosage 3 1 FeCl 3 dosage 3  1
Scenarios | 364 d-Average | Maximum daily average | Violations (days) | 364 d-Average | Maximum daily average | Violations (days) | (m d  ) | (m d )
Steady state REF | 0.20 |  |  | 15.02 |  |  | 3.0 2.0 | 3.0 2.0
REF | 0.84 | 4.06 | 1 | 16.85 | 47.67 | 9 | 3.0 e 6.0 | 2.0 e 4.0
EPC | 0.41 | 2.80 | 0 | 14.50 | 41.42 | 3 | 3.5 e 7.0 | 1.7 e 3.4
USS | 0.56 | 2.93 | 0 | 16.12 | 45.09 | 6 | 3.0 e 6.0 | 1.6 e 3.2
USS þ EPC | 0.30 | 1.82 | 0 | 13.97 | 41.04 | 3 | 3.0 e 6.0 | 1.4 e 2.8
USS þ EPC þ AGRI | 0.65 | 2.42 | 0 | 13.52 | 40.26 | 3 | 1.1 e 2.2 | 1.5 e 3.0
USS þ EPC þ ANA | 1.00 | 2.25 | 0 | 13.33 | 39.67 | 2 | e | 1.3 e 2.6
Scenarios | Biogas (m 3 h  1 ) | % Methane | Electricity from cogeneration (kWh m  3 ) | Electricity requirement (kWh m  3 ) | EROI a for electricity | Net energy requirement for entire life cycle | EROI LC b for the entire life cycle | EROI LC b for the entire life cycle
Steady state REF | 76.29 | 71.8 | 0.222 | 0.297 | 0.75 |  | e | e
REF | 68.22 | 76.4 | 0.203 | 0.311 | 0.65 | e | 0.11
EPC | 93.12 | 71.0 | 0.257 | 0.260 | 0.99 | 1.80 1.50 | 0.17
USS | 68.96 | 75.9 | 0.210 | 0.311 | 0.67 | 1.72 | 0.12
USS þ EPC | 93.95 | 70.5 | 0.266 | 0.258 | 1.03 | 1.33 | 0.20
USS þ EPC þ AGRI | 90.22 | 70.9 | 0.256 | 0.215 | 1.19 | 0.66 | 0.39
USS þ EPC þ ANA | 90.87 | 70.3 | 0.256 | 0.234 | 1.10 | 0.80 | 0.32
Scenarios | Nutrients from sludge c | Nutrients from sludge c | Nutrients from struvite | Nutrients from struvite | Nutrients from N-rich ef fl uent | Nutrients from N-rich ef fl uent | Total nutrients recovered | Total nutrients recovered
Scenarios | N (kgNm  3 ) | P (kg P 2 O 5 m  3 ) | N (kgNm  3 ) | P (kg P 2 O 5 m  3 ) | N (kg N m  3 ) | P (kg P 2 O 5 m  3 | N (kgNm  3 ) | P (kg P 2 O 5 m  3 )
Steady state REF | 4.49E-03 | 1.55E-02 | 0 | 0 | 0 | 0 | 4.49E-03 | 1.55E-02
REF | 4.57E-03 | 1.77E-02 | 0 | 0 | 0 | 0 | 4.57E-03 | 1.77E-02
EPC | 5.89E-03 | 1.82E-02 | 0 | 0 | 0 | 0 | 5.89E-03 | 1.82E-02
USS | 4.71E-03 | 1.62E-02 | 6.53E-04 | 3.31E-03 | 0 | 0 | 5.36E-03 | 1.95E-02
USS EPC | 5.94E-03 | 1.66E-02 | 6.53E-04 | 3.31E-03 | 0 | 0 | 6.59E-03 | 2.00E-02
þ USS þ EPC þ AGRI | 5.58E-03 | 1.66E-02 | 6.53E-04 | 3.31E-03 | 1.44E-02 | 7.73E-05 | 2.06E-02 | 2.00E-02
USS þ EPC þ ANA | 5.34E-03 | 1.52E-02 | 6.53E-04 | 3.31E-03 | 0 | 0 | 6.00E-03 | 1.85E-02