## Table_1
Parameter | Unit | Value
Average Flow | m^3/day | 45425
TSS 1 | g/m^3 | 215
cBOD5 2 | g/m^3 | 250
COD 1 | g/m^3 | 431
Ammonia N | g/m^3 | 11
Nitrite N 2 | g/m^3 | 0
Nitrate N 2 | g/m^3 | 0
TKN 1 | g/m^3 | 15.7
Soluble PO4-P 1 | g P/m^3 | 4.8
TP | g P/m^3 | 6
Total Alkalinity 2 | g CaCO3/m^3 | 250
Soluble Mg 2 | g/m^3 | 50
pH 2 | - | 7
DO 2 | g O2/m^3 | 0
Liquid Temperature | °C | 20

## Table_2
Unit Process | Design Parameters | Values
Grit chamber | Grit production per flow (m<sup>3</sup>/L) Dry solid content of grit (%) | 20 98
Anoxic reactors (Bioselectors) | Tank depth (m) Maximum volume (m<sup>3</sup>) | 4 2650 1
Plug-flow contact basins | Number of reactors in series Tank depth (m) Maximum volume (m<sup>3</sup>) | 3 4 6321
Plug-flow stabilization basins | Number of reactors in series Tank depth (m) Maximum volume (m<sup>3</sup>) | 3 4 3142
Secondary clarifiers | Surface area (m<sup>2</sup>) Tank depth (m) RAS/WAS 3 pumped flow (m<sup>3</sup>/day) | 2917.2 2 3 22,712
RAS/WAS pumping station | WAS pumped flow (m<sup>3</sup>/day) | 378.5
Dewatering | Underflow solids (mg/L) Solids removal efficiency (%) | 200,000 95
Disinfection | Volume (m<sup>3</sup>) Chlorine dosage (mg/L) | 844 6.0
Gravity thickener 4 | Surface area (m<sup>2</sup>) Tank depth (m) Underflow solids (mg/L) Removal efficiency (%) | 154.2 3 48,000 90
Anaerobic digester 4 | Maximum volume (m<sup>3</sup>) Temperature (°C) | 1500 35
Electrochemical struvite Reactor 5 | Section S1a-d | -
Solids separation 5 | Pumped flow (m<sup>3</sup>/day) Struvite removal efficiency (%) | 1 99

## Table_3
Scenario | Description | %Struvite Yield | H 2 Capture | Anaerobic Digestor
B1 | Existing treatment scheme in Ft. Smith | 0 | No | No
B2-45 | Existing treatment scheme with struvite production | 45 | No | No
B2-90 | Existing treatment scheme with struvite production | 90 | No | No
B3-45 | Existing treatment scheme with struvite production and H 2 capture | 45 | Yes | No
B3-90 | Existing treatment scheme with struvite production and H 2 capture | 90 | Yes | No
A1 | Existing treatment scheme with added anaerobic digestor | 0 | No | Yes
A2-45 | Added anaerobic digestor with struvite recovery | 45 | No | Yes
A3-90 | Added anaerobic digestor with struvite recovery | 90 | No | Yes
A3-45 | Added anaerobic digestor with struvite recovery and H 2 capture | 45 | Yes | Yes
A3-90 | Added anaerobic digestor with struvite recovery and H 2 capture | 90 | Yes | Yes

## Table_4
Cost Parameters | Value | Units | Source
Reactor | 1.73 | $ | [74,75]
Building Space | 0.43 | $ | [74,75]
Labor | 0.006 | h | [74,75]
Maintenance | 0.23 | $ | [74,75]
Mg (99.9%) | 3.24 | $ | [63-65]
Energy | 0.29 | $ | [66]

## Table_5
By-Product | B1 | B2-45 | B2-90 | B3-45 | B3-90 | A1 | A2-45 | A2-90 | A3-45 | A3-90
Struvite (kg/day) | - | 0.013 | 0.026 | 0.013 | 0.026 | 0 | 389 | 702 | 389 | 702
Hydrogen gas (L/day) | - | - | - | 1810 | 3590 | - | - | - | 52330 | 94500
Electricity, combustion of biogas (kWh) | - | - | - | - | - | 89.1 | 88.3 | 89.7 | 88.3 | 89.7
Heat, combustion of biogas (kWh) | - | - | - | - | - | 124.4 | 123.2 | 125.3 | 123.2 | 125.3
Phosphorus recovered in struvite (%) | - | ~0 | ~0 | ~0 | ~0 | - | 18 | 33 | 18 | 33

## Table_6
Cost Category | B1 | B2-45 | B2-90 | B3-45 | B3-90 | A1 | A2-45 | A2-90 | A3-45 | A3-90
Capital Costs
Standard Processes | $3,688,420 | $3,688,420 | $3,688,420 | $3,688,420 | $3,688,420 | $3,785,057 | $3,607,614 | $3,605,763 | $3,605,787 | $3,604,067
Sludge Management | $60,357 | $60,357 | $60,357 | $60,357 | $60,357 | $46,189 | $44,797 | $44,797 | $44,797 | $44,797
Anaerobic Digestion | $0 | $0 | $0 | $0 | $0 | $144,679 | $124,041 | $124,041 | $124,041 | $124,041
ECST Reactor | $0 | $11 | $21 | $11 | $21 | $0 | $307,108 | $554,500 | $307,108 | $554,500
H2 Compression | $0 | $0 | $0 | $119 | $162 | $0 | $0 | $0 | $13,401 | $17,590
H2 Storage | $0 | $0 | $0 | $0 | $1 | $0 | $0 | $0 | $11,114 | $20,066
Total Capital Cost | $3,748,777 | $3,748,788 | $3,748,798 | $3,748,907 | $3,748,961 | $3,975,925 | $4,083,560 | $4,329,101 | $4,106,248 | $4,365,062
O&M | $485,400 | $485,402 | $485,403 | $485,447 | $485,465 | $540,000 | $560,570 | $599,696 | $565,684 | $606,408
Materials | $598,063 | $598,596 | $599,483 | $598,596 | $599,483 | $530,248 | $493,634 | $482,719 | $495,763 | $485,559
Chemicals | $141,000 | $141,016 | $141,031 | $141,016 | $141,031 | $317,015 | $598,327 | $968,341 | $598,327 | $968,341
Energy | $202,720 | $204,248 | $203,786 | $204,248 | $203,786 | $171,036 | $212,991 | $240,074 | $213,828 | $241,583
Total Operational Cost | $1,427,183 | $1,429,261 | $1,429,704 | $1,429,306 | $1,429,766 | $1,558,299 | $1,865,522 | $2,290,829 | $1,873,603 | $2,301,891
Potential Revenues | $0 | $6 | $11 | $6 | $11 | $0 | $163,627 | $295,438 | $163,627 | $295,438
Struvite Fertilizer a | $0 | $6 | $11 | $6 | $11 | $0 | $163,627 | $295,438 | $163,627 | $295,438
H2 Gas b | $0 | $0 | $0 | $0 | $1 | $0 | $0 | $0 | $12,624 | $22,793
Total Revenue Net Cost | $0 | $6 | $11 | $6 | $12 | $0 | $163,627 | $295,438 | $176,251 | $318,230
$/year | $5,175,960 | $5,178,043 | $5,178,491 | $5,178,207 | $5,178,715 | $5,534,224 | $5,785,455 | $6,324,493 | $5,803,600 | $6,348,722
$/m3 | $0.31 | $0.31 | $0.31 | $0.31 | $0.31 | $0.33 | $0.35 | $0.38 | $0.35 | $0.38

## Table_7
| Struvite 1 ($/kg) | Hydrogen 2 ($/kg)
CAPEX | 2.16 | 13.22
O&M | 0.34 | 2.36
Magnesium Metal (99.9%) | 3.24 | -
Energy (electricity) | 0.29 | 0.01
Break-Even Price | 6.03 | 15.58