## Table_1
Parameters | Influent concen- trations (mg/l)* | Effluent concen- trations (mg/l)* | Effluent discharge standards (mg/l)**
BOD | 359.9 | 5.8 | 25
COD | 641.7 | 28.0 | 125
TSS | 261.2 | 7.1 | 35
TN | 57.5 | 3.3 | 10
TP | 9.1 | 0.9 | 1

## Table_2
Scenario category | Scenario number | Scenario description
Base | 0 | Current application
Operational changes | 1.1 | IR ratio reduction
| 1.2 | WAS flow rate reduction
| 1.3 | RAS flow rate reduction
| 1.4 | Re-aeration flow rate reduction (in OD4)
Structural changes | 2.1 | Replacing belt thickeners for gravity thickeners
| 2.2 | Replacing decanter for belt filters for dewatering
Configurational changes | 3.1 | Converting the process configuration to A2O
| 3.2 | Modified Bardenpho-5 configuration
| 3.3 | Removal of the sludge buffer tank

## Table_3
Effluent param- eter | Maximum error in predicted monthly treatment efficien- cies (%) | Average error in predicted treatment efficiencies (%)
COD | 2.1 | 1.2
BOD | 1.2 | 0.9
TSS | 1.5 | 0.8
TN | 5.3 | 0.8
TP | 10.6 | 3.6